## Index
CEYLON SHIPPING CORPORATION LTD.
MV CEYLON PRINCESS
DRY DOCK SPECIFICATION - 2ND RENEWAL DRY DOCK REPAIRS
ELECTRICAL REPAIRS (EL)
Job No | Description
CP/DD2/EL/001 | Main Switch board Service
CP/DD2/EL/002 | Emergency Generator Swith board Service
CP/DD2/EL/003 | Generator Alternator Service
CP/DD2/EL/004 | Valve Remote Control System
CP/DD2/EL/005 | Electrical Motors
CP/DD2/EL/006 | Cargo Crane Electrical Motors
CP/DD2/EL/007 | Transformer Service
CP/DD2/EL/008 | Cool Room Door Repairs
CP/DD2/EL/009 | MGPS anode replacement
CP/DD2/EL/010 | ICCP system
CP/DD2/EL/011 | Testing Engine Room Alarms
CP/DD2/EL/012 | Fire Detection Syatem
CP/DD2/EL/013 | ER Watermist System

## CP-DD2-EL -001
MV "CEYLON PRINCESS" | SPECIFICATION OF REPAIRS
JOB NUMBER | DATE |  | Authorized by | Signature |  | PANEL NAME | AMMETER | VOLT METER | kW METERS | FREQUENCY METER | POWER FACTOR METER | AC220V BUS BAR INSULATION METER | AC440V BUS BAR INSULATION METER | DC24V INSULATION METER
CP-DD2- EL -001 |  |  | Chamindra Silva Technical Superintendent
JOB TITLE: Main Switch Board Maintenmance |  | TO BE INCLUDED |  |  | RANGE
MAKERS DETAILS, SERIAL NO, MACHINERY / EQUIPMEN DETAILS. |  | SPECIAL REQUIREMENT |  |  | 55-65Hz,440V | MAIN SWITCHBOARD | 4 | 5 | 6 | 5 | 3 | 1 | 1
MAIN SWITCH BOARD MAKER: Zhenjiang Saiernico Slectric Co. Ltd. TYPE: JZB-700x3/14 ACB MAKER: Mitsubishi TYPE: Mitsubishi AE1600-SW - 3 nos |  |  | Gas free certificate |  | 0 - 500A, 500/5A, 60Hz | EMERGENCY SWITCHBOARD | 2 | 2 | 1 | 1 | 1 | 1 | 1
|  | X | Lighting |  | 0-600V | GUPS | 1 | 1 | [5 empty] | 1
|  |  | Ventilation |  | 0-1500A, 1500/5A, | BATTERY CHARGING & DISCHARGING | 1 | 1 | [5 empty] | 1
|  | X | Access work |  | 0 - 600V
|  |  | Staging |  | 150-0Kw 0-1000Kw, 1500/5A
LOCATION: |  |  | Open manhole(s) |  | 55 - 65Hz, 440V
DETAILED SPECIFICATION INCL.SIZE,AMOUNT,DIMENSION,MATERIAL,ETC. |  |  | Dismantle floorplate(s) |  | 0.5-1 CAPACITANCE,1-0.5 IMPEDENCE
|  |  | Cleaning before |  | 0-1500A, 1500/5A,
1. Main switch board to be serviced. 2. All meters to be calibrated. a) KW meters b) Volt meter c) Ampere meters d) Frequency Meters 3. Main switch board ACB’s be serviced. 4. Thermographic inspection to be done and report to be issued. 5. ACB Below safety functions to be carried out to the satisfaction to the attending Class Surveyor. a) High & Under voltage trip. b) - Over current c) - Reverse power trip. d) - Preferential trip. e) - High & low frequency ACB type : Mitsubishi AAE1600-SW / 450 V-3 Phase/ 700KW/ 1123 A- 3nos. |  | X | Cleaning after |  | 0 - 600V
|  |  | Crane |  | 150-0Kw 0-1000Kw, 1500/5A
|  |  | Internal transport |  | 55 - 65Hz, 440V
|  |  | Transport outside yard |  | 0.5-1 CAPACITANCE,1-0.5 IMPEDENCE
|  |  | Paintwork |  | 0-1500A, 1500/5A,
|  |  | Pressure Testing |  | 0 - 600V
|  | X | Function Testing |  | 150-0Kw 0-1000Kw, 1500/5A
|  |  | Fire watch |  | 55 - 65Hz, 440V
|  |  | Insulation off/on |  | 0.5-1 CAPACITANCE,1-0.5 IMPEDENCE
|  | THE WORK TO BE SURVEYED |  |  | 150-0Kw 0-1000Kw, 1500/5A
|  | X | Class Representative |  | 150-0Kw 0-1000Kw, 1500/5A
|  |  | Maritime Autorities |  | 150-0Kw 0-1000Kw, 1500/5A
|  |  | Manufacturer |  | 0-600V
|  | X | Owners representative |  | 55-65Hz , 440V
|  | ATTACHEMNTS |  |  | INFINITY - 0 M/Ohm , 440V
|  | X | Photo
|  | X | Drawing
Sketch
Sample
MATERIAL SUPPLIED BY
|  | X | Yard
Owner
REMARKS:
RANGE
0-250A , 250/5A , 60Hz
0-600V
INFINITY - 0 M/Ohm
0-150Kw, 440V, 250/5A, 60Hz
55-65Hz , 440V
0-150A, 150/5A, 60Hz
INFINITY - 0 M/Ohm, 220V
0-300V
RANGE
0-100A
0-50V
INFINITY - 0 M/OHM,DC24V
0-100A
INFINITY - 0 M/OHM,DC24V
0-50V

## CP-DD2-EL -002
MV "CEYLON PRINCESS" | SPECIFICATION OF REPAIRS
JOB NUMBER | DATE |  | Authorized by | Signature
CP-DD2- EL -002 |  |  | Chamindra Silva Technical Superintendent
JOB TITLE: Emergency Switch Board Service |  | TO BE INCLUDED
MAKERS DETAILS, SERIAL NO, MACHINERY / EQUIPMEN DETAILS. |  | SPECIAL REQUIREMENT
SaierNico Marine Switch board Maker: Zhenjiang Saiernico Electric Co. LTD Type : JYB-120 X 1/3 Gen. Power : 120 kW x 1 Volt : 450 V/230V, 60 Hz |  |  | Gas free certificate
|  | X | Lighting
Ventilation
|  | X | Access work
Staging
LOCATION: |  |  | Open manhole(s)
DETAILED SPECIFICATION INCL.SIZE,AMOUNT,DIMENSION,MATERIAL,ETC. |  |  | Dismantle floorplate(s)
Cleaning before
1. Emergency switch board to be serviced. 2. All meters to be calibrated. a) KW meters b) Volt meter c) Ampere meters d) Frequency Meters 3. Switch board ACB’s be serviced. 4. Thermographic inspection to be done and report to be issued. 5. ACB Below safety functions to be carried out to the satisfaction to the attending Class Surveyor. a) High & Under voltage trip. b) - Over current c) - Reverse power trip. d) - Preferential trip. e) - High & low frequency ACB type : Mitsubishi AE630-SW / 450V - 1 nos. |  | X | Cleaning after
Crane
Internal transport
Transport outside yard
Paintwork
Pressure Testing
|  | X | Function Testing
Fire watch
Insulation off/on
THE WORK TO BE SURVEYED
|  | X | Class Representative
Maritime Autorities
Manufacturer
|  | X | Owners representative
ATTACHEMNTS
|  | X | Photo
|  | X | Drawing
Sketch
Sample
MATERIAL SUPPLIED BY
|  | X | Yard
Owner
REMARKS:

## CP-DD2-EL -003
MV "CEYLON PRINCESS" | SPECIFICATION OF REPAIRS
JOB NUMBER | DATE |  | Authorized by | Signature
CP-DD2- EL -003 |  |  | Chamindra Silva Technical Superintendent
JOB TITLE: Generator Alternator |  | TO BE INCLUDED
MAKERS DETAILS, SERIAL NO, MACHINERY / EQUIPMEN DETAILS. |  | SPECIAL REQUIREMENT
MAKER :LEROY-SOMER Three phase Brushless Synchronus Alternators Type: HFC6 504-14k Rated output :450V/60Hz, 875kVA Rated Speed :720r/min |  |  | Gas free certificate
|  | x | Lighting
|  | x | Ventilation
|  | x | Access work
Staging
LOCATION: |  |  | Open manhole(s)
DETAILED SPECIFICATION INCL.SIZE,AMOUNT,DIMENSION,MATERIAL,ETC. |  |  | Dismantle floorplate(s)
|  | x | Cleaning before
Generator alternator following jobs to be carried out - 03 Nos a). All wires to be disconnected insulation resistance and air gaps to be measured and recorded before and after the job. b). Complete Alternator to be serviced (including the exciter) and insulation to be improved. c). After completion of service test run to be carried. d). Generator to be load tested. |  | x | Cleaning after
Crane
Internal transport
Transport outside yard
Paintwork
Pressure Testing
|  | x | Function Testing
Fire watch
Insulation off/on
THE WORK TO BE SURVEYED
|  | x | Class Representative
Maritime Autorities
Manufacturer
|  | x | Owners representative
ATTACHEMNTS
Photo
|  | x | Drawing
Sketch
Sample
MATERIAL SUPPLIED BY
|  | X | Yard
Owner
REMARKS:

## CP-DD2-EL -004
MV "CEYLON PRINCESS" | SPECIFICATION OF REPAIRS
JOB NUMBER | DATE |  | Authorized by | Signature
CP-DD2- EL -004 |  |  | Chamindra Silva Technical Superintendent
JOB TITLE: Valve Remote Control System |  | TO BE INCLUDED
MAKERS DETAILS, SERIAL NO, MACHINERY / EQUIPMEN DETAILS. |  | SPECIAL REQUIREMENT
MAKER : PLEIGER FAR EAST LTD |  |  | Gas free certificate
|  | X | Lighting
Ventilation
|  | X | Access work
Staging
LOCATION: |  |  | Open manhole(s)
DETAILED SPECIFICATION INCL.SIZE,AMOUNT,DIMENSION,MATERIAL,ETC. |  |  | Dismantle floorplate(s)
|  | X | Cleaning before
1. VRCS system control cabinet health checkup. 2. VRCS system solenoid valve cabinet health checkup. 3. VRCS system ecr and ships office pc opening/closing of remote valve indication and operation to be checked 4. VRCS system ams / bcc alarms to be rectified |  |  | Cleaning after
Crane
Internal transport
Transport outside yard
Paintwork
Pressure Testing
|  | X | Function Testing
Fire watch
Insulation off/on
THE WORK TO BE SURVEYED
Class Representative
Maritime Autorities
Manufacturer
|  | X | Owners representative
ATTACHEMNTS
Photo
|  | X | Drawing
Sketch
Sample
MATERIAL SUPPLIED BY
|  | X | Yard
Owner
REMARKS:

## CP-DD2-EL -005
MV "CEYLON PRINCESS" | SPECIFICATION OF REPAIRS |  |  |  | ENGINE ROOM MOTORS
JOB NUMBER | DATE |  | Authorized by | Signature | MOTOR | KW | BEARING NUMBER |  | LOCATOIN
CP-DD2- EL -005 |  |  | Chamindra Silva Technical Superintendent |  |  |  | DE | NDE
JOB TITLE: Electrical Motors |  | TO BE INCLUDED |  |  | MAIN LUB OIL PUMP 01 | 90 | 6316/C3 | 6316/C3 | Tank Top
MAKERS DETAILS, SERIAL NO, MACHINERY / EQUIPMEN DETAILS. |  | SPECIAL REQUIREMENT |  |  | MAIN LUB OIL PUMP 02 | 90 | 6316/C3 | 6316/C3 | Tank Top
Motors List Is Attached |  |  | Gas free certificate |  | BALLAST PUMP 01 | 99 | 6316/C3 | 6316/C3 | Engine Lower Flat
|  |  | Lighting |  | BALLAST PUMP 02 | 99 | 6316/C3 | 6316/C3 | Engine Lower Flat
|  |  | Ventilation |  | FIRE AND GS PUMP | 55 | 6316/C3 | 6316/C3 | Engine Lower Flat
|  | X | Access work |  | BILGE AND GS PUMP | 55 | 6316/C3 | 6316/C3 | Engine Bottom Flat
|  | X | Staging |  | M/E JACKET F/W PREHEATER PUMP | 2.2 | 6205DDU/C3 | 6205DDU/C3 | Engine Middle Flat
LOCATION: |  |  | Open manhole(s) |  | MAIN ENGINE JACKET WATER PUMP 01 | 18.5 | 63102Z/C3 | 63102Z/C3 | Engine Middle Flat
DETAILED SPECIFICATION INCL.SIZE,AMOUNT,DIMENSION,MATERIAL,ETC. |  |  | Dismantle floorplate(s) |  | MAIN ENGINE JACKET WATER PUMP 02 | 18.5 | 63102Z/C3 | 63102Z/C3 | Engine Middle Flat
|  | X | Cleaning before |  | HFO TRANSFER PUMP | 18.5 | 63102Z/C3 | 63102Z/C3 | Engine Manoeuvering Flat
Motors to be isolated and fuses removed. Motors to be removed to yard workshop and returned back without delay on completion of work. Motors be dismantled and cleaned. Non-inflammable electrical solvent is to be used for cleaning the windings. Windings there after dried and varnished and baked. Record insulation readings before and after the overhaul. Both bearings are to be renewed by ship supply. Allow for resleaving of 2 bearing housings. Dynamic balancing of rotor to be carried out in presence of Chief engineer. Assemble motors in place and carry out alignment. After completion, satisfactory load test to be shown in presence of Chief engineer. Reports to be provided. Removal and refit of railings in way of motor shall be included. QUOTE TOTAL COST AS PER SCOPE a. Cost of overhaul per motor b. Cost of dynamic balancing c. Cost of resleeving one bearing housing. |  | X | Cleaning after |  | MDO TRANSFER PUMP | 18.5 | 63102Z/C3 | 63102Z/C3 | Engine Manoeuvering Flat
|  | X | Crane |  | MAIN SEA WATER PUMP 01 | 37 | 63102Z/C3 | 63102Z/C3 | Engine Lower Flat
|  | X | Internal transport |  | MAIN SEA WATER PUMP 02 | 37 | 63102Z/C3 | 63102Z/C3 | Engine Lower Flat
|  |  | Transport outside yard |  | MAIN SEA WATER PUMP 03 | 37 | 63102Z/C3 | 63102Z/C3 | Engine Lower Flat
|  |  | Paintwork |  | L.T.COOLING WATER PUMP 01 | 45 | 63102Z/C3 | 63102Z/C3 | Engine Middle Flat
|  |  | Pressure Testing |  | L.T.COOLING WATER PUMP 02 | 45 | 63102Z/C3 | 63102Z/C3 | Engine Middle Flat
|  | X | Function Testing |  | L.T.COOLING WATER PUMP 03 | 45 | 63102Z/C3 | 63102Z/C3 | Engine Middle Flat
|  |  | Fire watch |  | FRESH WATER HYDROPORE PUMP 01 | 5.5 | 6208DDU/C3 | 6208DDU/C3 | Engine Middle Flat
|  |  | Insulation off/on |  | FRESH WATER HYDROPORE PUMP 02 | 5.5 | 6208DDU/C3 | 6208DDU/C3 | Engine Middle Flat
|  | THE WORK TO BE SURVEYED |  |  | LSMGO TRANSFER PUMP | 7.5 | 6208DDU/C3 | 6208DDU/C3 | Engine Manoeuvering Flat
|  |  | Class Representative |  | ME AUXILIARY BLOWER MOTOR | 54 | 6312/C3 | 6312/C3 | Engine Manoeuvering Flat
|  |  | Maritime Autorities |  | ME AUXILIARY BLOWER MOTOR | 54 | 6312/C3 | 6312/C3 | Engine Manoeuvering Flat
|  |  | Manufacturer |  | HFO PURIFIER MOTOR 01 | 5.5 | 6208ZZ | 6208ZZ | Purifire Flat
|  | X | Owners representative |  | HFO PURIFIER MOTOR 02 | 5.5 | 6208ZZ | 6208ZZ | Purifire Flat
|  | ATTACHEMNTS |  |  | LO PURIFIER MOTOR 01 | 4 | 6208ZZ | 6208ZZ | Purifire Flat
|  |  | Photo |  | LO PURIFIER MOTOR 02 | 4 | 6208ZZ | 6208ZZ | Purifire Flat
|  | X | Drawing |  | SEWAGE PUMP | 2.2 | 6208ZZ | 6208ZZ | Engine Manoeuvering Flat
|  |  | Sketch |  | FRESH WATER GENERATOR DISTILLATE PUMP | 1.5 | 6205ZZC2 | 6205ZZC2 | Engine Middle Flat
|  |  | Sample |  | R.O PLANT HIGH PRESSURE PUMP | 5.5 | 6208-ZZ/C3 | 6206-ZZ/C3 | Engine Middle Flat
|  | MATERIAL SUPPLIED BY |  |  | O.W.S. BILGE PUMP | 1.5 | 6206DDU/C3 | 6206DDU/C3 | Engine Lower Flat
|  | X | Yard |  | SLUDGE PUMP | 2.2 | 6207DDU/C3 | 6207DDU/C3 | Engine Lower Flat
|  |  | Owner |  | DAILY BILGE PUMP | 2.2 | 6207DDU/C3 | 6207DDU/C3 | Engine Lower Flat
REMARKS: |  |  |  |  | TECHNICAL WATER PUMP 01 | 3.7 | 6207DDU/C3 | 6207DDU/C3 | Engine Middle Flat
[5 empty] | TECHNICAL WATER PUMP 02 | 3.7 | 6207DDU/C3 | 6207DDU/C3 | Engine Middle Flat
[5 empty] | STEERING GEAR MOTOR 01 | 37 | 6313ZZ | 6312ZZ | Steeing Gear Room
[5 empty] | STEERING GEAR MOTOR 02 | 37 | 6313ZZ | 6312ZZ | Steeing Gear Room
[5 empty] | BOILER COMBUTION FAN MOTOR | 8.7 | 6308 ZZ | 6308 ZZ | Engine Casing
[5 empty] | MAIN AIR COMPRESSOR 01 | 52.4 | 6317/C3 | 6314/C3 | E/R Upper Platform
[5 empty] | MAIN AIR COMPRESSOR 02 | 52.4 | 6317/C3 | 6314/C3 | E/R Upper Platform
[5 empty] | EMERGENCY AIR COMPRESSOR | 6.3 | 6308-2Z/C3WT | 6308-2Z/C3WT | E/R Upper Platform
[5 empty] | LO TRANSFER PUMP MOTOR | 2.2 | 6207DDU/C3 | 6207DDU/C3 | Engine Lower Flat
[5 empty] | CYLINDER LO TRANSFER PUMP MOTOR | 0.75 | 6205DDU/C3 | 6205DDU/C3 | Workshop Store
[5 empty] | E/R BLOWER FAN MOTOR 01 | 22 | 6311 Z | 6311 Z | Engine Blower room 01
[5 empty] | E/R BLOWER FAN MOTOR 02 | 22 | 6311 Z | 6311 Z | Engine Blower room 01
[5 empty] | E/R BLOWER FAN MOTOR 03 | 22.2 | 6311 Z | 6311 Z | Engine Blower room 02
[5 empty] | E/R BLOWER FAN MOTOR 04 | 22 | 6311 Z | 6311 Z | Engine Blower room 02
CRANE MOTORS
[5 empty] | MOTOR | KW | BEARING NUMBER |  | LOCATOIN
[7 empty] | DE | NDE
[5 empty] | Deck crane main Electric motor (04) | 203 | 6319 C3 | 7319 AC | All 4 deck cranes
[5 empty] | crane Oil Cooler fan Motor (040 | 2.2 |  |  | All 4 deck cranes
DECK ELECTRIC MOTORS
[5 empty] | MOTOR | KW | BEARING NUMBER |  | LOCATOIN
[7 empty] | DE | NDE
[5 empty] | EMERGENCY FIRE PUMP | 30 | 6312 ZZ/C3 | 6312 ZZ/C3 | FORCASTLE
[5 empty] | PORT SIDE PILOT LADDER WINCH MOTOR |  | 6307ZZ | 6307ZZ | MAIN DECK PORT SIDE
[5 empty] | STBD SIDE PILOT LADDER WINCH MOTOR |  | 6307ZZ | 6307ZZ | MAIN DECK STBD SIDE
[5 empty] | PORT SIDE GANGWAY LADDER WINCH MOTOR | 2.5 | 6307ZZ | 6307ZZ | DECK PORT SIDE
[5 empty] | STBD SIDE GANGWAY LADDER WINCH MOTOR | 2.5 | 6307ZZ | 6307ZZ | DECK STBD SIDE
[5 empty] | AC PLANT BLOWER MOTOR 01 | 11 | 6307ZZ | 6309ZZ | ACCOMMODATION U/DECK
[5 empty] | AC PLANT BLOWER MOTOR 02 | 11 | 6307ZZ | 6309ZZ | ACCOMMODATION U/DECK
[5 empty] | PROVISION CRANE TRAVELLINBG MOTOR (2M1) | 4 | NOT SPECIFIED | NOT SPECIFIED | ACCOMMODATION AFT A/DECK
[5 empty] | PROVISION CRANE WINCH MOTOR - A (3M1) | 13 | NOT SPECIFIED | NOT SPECIFIED | ACCOMMODATION AFT A/DECK
[5 empty] | PROVISION CRANE WINCH MOTOR - B (3M2) | 13 | NOT SPECIFIED | NOT SPECIFIED | ACCOMMODATION AFT A/DECK

## CP-DD2-EL -006
MV "CEYLON PRINCESS" | SPECIFICATION OF REPAIRS
JOB NUMBER | DATE |  | Authorized by | Signature
CP-DD2- EL -006 |  |  | Chamindra Silva Technical Superintendent
JOB TITLE: Cargo Crane Motors |  | TO BE INCLUDED
MAKERS DETAILS, SERIAL NO, MACHINERY / EQUIPMEN DETAILS. |  | SPECIAL REQUIREMENT
Cargo Crane – Macgregor KW- 203 Bearing Number – 6319 C3 / 7319 AC |  |  | Gas free certificate
|  | X | Lighting
Ventilation
|  | X | Access work
|  | X | Staging
LOCATION: |  |  | Open manhole(s)
DETAILED SPECIFICATION INCL.SIZE,AMOUNT,DIMENSION,MATERIAL,ETC. |  |  | Dismantle floorplate(s)
|  | X | Cleaning before
Motors to be isolated and fuses removed. Motors to be removed from the cranes and to be transported to yard workshop and returned back without delay on completion of work. Motors be dismantled and cleaned. Non-inflammable electrical solvent is to be used for cleaning the windings. Windings there after dried and varnished and baked. Record insulation readings before and after the overhaul. Both bearings are to be renewed by ship supply. Allow for resleeving of 2 bearing housings. Dynamic balancing of rotor to be carried out in presence of Chief engineer. Assemble motors in place and carry out alignment. After completion, satisfactory load test to be shown in presence of Chief engineer. Reports to be provided. Yard technicians to be present at the crane load test to monitor motor condition. Removal and refit of railings and Crane Cabin, to take motors out of the crane house in way of motors shall be included. QUOTE TOTAL COST AS PER SCOPE a. Cost of overhaul per motor b. Cost of dynamic balancing c. Cost of resleeving one bearing housing. d. Remove and refix crane cabin Cargo Crane – Macgregor o4 Motors (01 motor each crane) |  | X | Cleaning after
|  | X | Crane
|  | X | Internal transport
Transport outside yard
|  | X | Paintwork
Pressure Testing
|  | X | Function Testing
Fire watch
Insulation off/on
THE WORK TO BE SURVEYED
Class Representative
Maritime Autorities
Manufacturer
|  | X | Owners representative
ATTACHEMNTS
|  | X | Photo
|  | X | Drawing
Sketch
Sample
MATERIAL SUPPLIED BY
|  | X | Yard
Owner
REMARKS:
Cranes to be Parked safly, before removing the Motors. Cranes are parked should not hamper the works carrid out onboard. Once remove the crane cabin temporarly covering to be done to protect inside the crane.

## CP-DD2-EL -007
MV "CEYLON PRINCESS" | SPECIFICATION OF REPAIRS
JOB NUMBER | DATE |  | Authorized by | Signature
CP-DD2- EL -007 |  |  | Chamindra Silva Technical Superintendent
JOB TITLE: Transformer Service |  | TO BE INCLUDED
SPECIAL REQUIREMENT
Gas free certificate
|  | X | Lighting
|  | X | Ventilation
|  | X | Access work
Staging
LOCATION: |  |  | Open manhole(s)
DETAILED SPECIFICATION INCL.SIZE,AMOUNT,DIMENSION,MATERIAL,ETC. |  |  | Dismantle floorplate(s)
|  | X | Cleaning before
Transformers to be serviced by yard. All connection tightness to be checked. Insulation resistance to be checked. Cleaning of transformers to be done. Earth bonding strap connection to be serviced. 1. General Transformer CSD – 135 (02 Nos) 2. Emergency Transformer CSD – 35 (02 Nos) |  | X | Cleaning after
Crane
Internal transport
Transport outside yard
Paintwork
Pressure Testing
|  | X | Function Testing
|  | X | Fire watch
Insulation off/on
THE WORK TO BE SURVEYED
Class Representative
Maritime Autorities
Manufacturer
|  | X | Owners representative
ATTACHEMNTS
Photo
|  | X | Drawing
Sketch
Sample
MATERIAL SUPPLIED BY
|  | X | Yard
Owner
REMARKS:

## CP-DD2-EL -008
MV "CEYLON PRINCESS" | SPECIFICATION OF REPAIRS
JOB NUMBER | DATE |  | Authorized by | Signature
CP-DD2- EL -008 |  |  | Chamindra Silva Technical Superintendent
JOB TITLE: Cool room Doors |  | TO BE INCLUDED
MAKERS DETAILS, SERIAL NO, MACHINERY / EQUIPMEN DETAILS. |  | SPECIAL REQUIREMENT
Gas free certificate
Lighting
Ventilation
|  | X | Access work
Staging
LOCATION: |  |  | Open manhole(s)
DETAILED SPECIFICATION INCL.SIZE,AMOUNT,DIMENSION,MATERIAL,ETC. |  |  | Dismantle floorplate(s)
|  | X | Cleaning before
Quote to carry out, cool room door sealing Rubber Elements; Door alignments must be adjusted as appropriate and sealing to be confirmed. 1. Meat room, 2. Fish room, 3. Vegetable room, 4. Dry room, sealing rubber elements must be replaced. |  | X | Cleaning after
Crane
Internal transport
Transport outside yard
Paintwork
Pressure Testing
|  | X | Function Testing
Fire watch
Insulation off/on
THE WORK TO BE SURVEYED
Class Representative
Maritime Autorities
Manufacturer
|  | X | Owners representative
ATTACHEMNTS
Photo
Drawing
Sketch
Sample
MATERIAL SUPPLIED BY
|  | X | Yard
Owner
REMARKS:

## CP-DD2-EL -009
MV "CEYLON PRINCESS" | SPECIFICATION OF REPAIRS
JOB NUMBER | DATE |  | Authorized by | Signature
CP-DD2- EL -009 |  |  | Chamindra Silva Technical Superintendent
JOB TITLE: GGPS anodes |  | TO BE INCLUDED
MAKERS DETAILS, SERIAL NO, MACHINERY / EQUIPMEN DETAILS. |  | SPECIAL REQUIREMENT
Maker: K.C.LTD 1589-6,SONGJUNG-DONG,KANGSU-KU,BUSAN 618-270,KOREA TEL-+82518317720 FAX-+82518317726 |  |  | Gas free certificate
Lighting
Ventilation
|  | X | Access work
Staging
LOCATION: |  |  | Open manhole(s)
DETAILED SPECIFICATION INCL.SIZE,AMOUNT,DIMENSION,MATERIAL,ETC. |  |  | Dismantle floorplate(s)
|  | X | Cleaning before
The antifouling system consists of one Marine Growth Anodes (MG) and one Trap Corrosion Anodes (TC) located in each sea chest P & S. Yard is to tender for the exchange all of MG and TC anodes (total (4) pieces) with Owner’s supply anodes. Ship staff must witness the anode fitting to avoid misunderstanding on sealing work. Quote all-inclusive price 1. MGPS System Anodes to be replaced. 2. System Service to be carried out. |  | X | Cleaning after
Crane
Internal transport
Transport outside yard
Paintwork
|  | X | Pressure Testing
|  | X | Function Testing
Fire watch
Insulation off/on
THE WORK TO BE SURVEYED
|  | X | Class Representative
Maritime Autorities
Manufacturer
|  | X | Owners representative
ATTACHEMNTS
Photo
|  | X | Drawing
Sketch
Sample
MATERIAL SUPPLIED BY
|  | X | Yard
Owner
REMARKS:

## CP-DD2-HL-010
MV "CEYLON PRINCESS" | SPECIFICATION OF REPAIRS
JOB NUMBER | DATE |  | Authorized by | Signature
CP-DD2-HL-010 |  |  | Chamindra Silva Technical Superintendent
JOB TITLE: ICCP Anode / Reference electrode renewal and Service |  | TO BE INCLUDED
SPECIAL REQUIREMENT
Gas free certificate
Maker: K.C.LTD 1589-6,SONGJUNG-DONG,KANGSU-KU,BUSAN 618-270,KOREA TEL-+82518317720 FAX-+82518317726 |  |  | Lighting
Ventilation
|  | X | Access work
|  | X | Staging
Open manhole(s)
DETAILED SPECIFICATION INCL.SIZE,AMOUNT,DIMENSION,MATERIAL,ETC. |  |  | Dismantle floorplate(s)
|  | X | Cleaning before
Carry out the 10-year servicing of the Impressed Current Cathodic Protection (ICCP) system, including inspection, testing, calibration, and renewal of the Anode and the reference electrode. Open the cofferdam lid and inspect any sign of sea water leakage inside cofferdam. Dielectric shield to be inspected. Shaft grounding assembly to be inspected. Secure di-electric shield area around anode good. If necessary, apply epoxy putty along the gap between resin encapsulation of anode/ref. electrode cell and di-electric shield. All disturbed or repaired areas, including ICCP fittings, to be properly surface prepared and coated with Cathelcoshield Epoxy Filler (A+B) to be applied (Yard Supply). Submit all test reports on completion. Final tuning to be carried out once the vessel is afloat. Quote Lump sum price for the whole job including staging or cherry picker required. |  | X | Cleaning after
|  | X | Crane
Internal transport
Transport outside yard
|  | X | Paintwork
|  | X | Pressure Testing
|  | X | Function Testing
Fire watch
Insulation off/on
THE WORK TO BE SURVEYED
|  | X | Class Representative
Maritime Autorities
Manufacturer
|  | X | Owners representative
ATTACHEMNTS
Photo
|  | X | Drawing
Sketch
Sample
MATERIAL SUPPLIED BY
|  | X | Yard
Owner
REMARKS:

## CP-DD2-EL -011
MV "CEYLON PRINCESS" | SPECIFICATION OF REPAIRS
JOB NUMBER | DATE |  | Authorized by | Signature
CP-DD2- EL -11 |  |  | Chamindra Silva Technical Superintendent
JOB TITLE: Engine Room Alarms |  | TO BE INCLUDED
MAKERS DETAILS, SERIAL NO, MACHINERY / EQUIPMEN DETAILS. |  | SPECIAL REQUIREMENT
Gas free certificate
Lighting
Ventilation
|  | X | Access work
Staging
LOCATION: |  |  | Open manhole(s)
DETAILED SPECIFICATION INCL.SIZE,AMOUNT,DIMENSION,MATERIAL,ETC. |  |  | Dismantle floorplate(s)
Cleaning before
All engine room alarms to be tested. Quote as follows 1. Boiler Alarms 2. ME engine warning Alarms 3. AE Warning alarms 4. Fire alarms 5. ER Bilge Alarms |  |  | Cleaning after
Crane
Internal transport
Transport outside yard
Paintwork
Pressure Testing
|  | X | Function Testing
Fire watch
Insulation off/on
THE WORK TO BE SURVEYED
|  | X | Class Representative
Maritime Autorities
Manufacturer
|  | X | Owners representative
ATTACHEMNTS
Photo
Drawing
Sketch
Sample
MATERIAL SUPPLIED BY
|  | X | Yard
Owner
REMARKS:

## CP-DD2- EL-012
MV "CEYLON PRINCESS" | SPECIFICATION OF REPAIRS
JOB NUMBER | DATE |  | Authorized by | Signature
CP-DD2-DK -040 |  |  | Chamindra Silva Technical Superintendent
JOB TITLE: Fire detection system Service |  | TO BE INCLUDED
MAKERS DETAILS, SERIAL NO, MACHINERY / EQUIPMEN DETAILS. |  | SPECIAL REQUIREMENT
Maker - CONSILIUM Product Batch/Serial number - F400-101-10103A 90312 System - CCP FDS ANALOG Software - FDS_1.8.0 |  |  | Gas free certificate
Lighting
Ventilation
|  | X | Access work
Staging
LOCATION: |  |  | Open manhole(s)
DETAILED SPECIFICATION INCL.SIZE,AMOUNT,DIMENSION,MATERIAL,ETC. |  |  | Dismantle floorplate(s)
|  | X | Cleaning before
Fire detection sytem to health Checked and service. 1. By yard technician. 2. By makers technicians |  | X | Cleaning after
Crane
Internal transport
Transport outside yard
Paintwork
Pressure Testing
|  | X | Function Testing
Fire watch
Insulation off/on
THE WORK TO BE SURVEYED
|  | X | Class Representative
Maritime Autorities
Manufacturer
|  | X | Owners representative
ATTACHEMNTS
Photo
Drawing
|  | X | Sketch
Sample
MATERIAL SUPPLIED BY
|  | X | Yard
Owner
REMARKS:

## CP-DD2- EL- 013
MV "CEYLON PRINCESS" | SPECIFICATION OF REPAIRS
JOB NUMBER | DATE |  | Authorized by | Signature
CP-DD2-DK -041 |  |  | Chamindra Silva Technical Superintendent
JOB TITLE: ER Watermist System |  | TO BE INCLUDED
MAKERS DETAILS, SERIAL NO, MACHINERY / EQUIPMEN DETAILS. |  | SPECIAL REQUIREMENT
Maker : Tyco Seaplus Co., Ltd. Series : AVIC398/399(DNV) |  |  | Gas free certificate
Lighting
Ventilation
|  | X | Access work
Staging
LOCATION: |  |  | Open manhole(s)
DETAILED SPECIFICATION INCL.SIZE,AMOUNT,DIMENSION,MATERIAL,ETC. |  |  | Dismantle floorplate(s)
|  | X | Cleaning before
Carry out 10-year service of water mist system to be carried out by Manufacturers recommended, Class DNV approved Team that to be arrange by the yard o All valve function to be verified for remote & local operation. o All fire detectors in system to be cleaned and health check o The pump to be serviced and operation to be verified o All nozzles to be cleaned o All pipe work to be cleaned Quote Lump Sum Price |  | X | Cleaning after
Crane
Internal transport
Transport outside yard
Paintwork
Pressure Testing
|  | X | Function Testing
Fire watch
Insulation off/on
THE WORK TO BE SURVEYED
|  | X | Class Representative
Maritime Autorities
Manufacturer
|  | X | Owners representative
ATTACHEMNTS
Photo
|  | X | Drawing
Sketch
Sample
MATERIAL SUPPLIED BY
|  | X | Yard
Owner
REMARKS: